## Full comparison
capacity_kwh | Solar_kw_DC | Solar_kw_AC | EV_load_scenario | total_load_kwh | total_pv_kwh | pv_curtailed_kwh | pv_used_kwh | energy_not_served_kwh | self_sufficiency_percent | pv_utilization_percent | throughput_charge_kwh | throughput_discharge_kwh | estimated_full_cycles | loss_of_load_hours | max_contiguous_lol_hours
100 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 263171 | 128469.86 | 9063.51 | 93 | 33 | 25870.76 | 23880.89 | 124.18 | 3223 | 36
200 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 255762.66 | 135878.2 | 2262.91 | 98 | 35 | 33279.1 | 30681.49 | 79.87 | 634 | 21
300 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 254085.7 | 137555.16 | 765.42 | 99 | 35 | 34956.06 | 32178.98 | 55.87 | 202 | 18
400 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 253569.92 | 138070.94 | 338.08 | 100 | 35 | 35471.84 | 32606.32 | 42.46 | 71 | 17
500 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 253366.14 | 138274.72 | 198.28 | 100 | 35 | 35675.62 | 32746.12 | 34.11 | 32 | 16
600 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 253220.31 | 138420.55 | 111.88 | 100 | 35 | 35821.45 | 32832.52 | 28.5 | 29 | 14
700 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 253074.47 | 138566.39 | 25.48 | 100 | 35 | 35967.29 | 32918.92 | 24.49 | 17 | 8
800 | 259.2 | 185.1429 | Med | 135543.5 | 391640.86 | 252994.74 | 138646.12 | 0 | 100 | 35 | 36047.02 | 32944.4 | 21.45 | 0 | 0
100 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 218043.42 | 173597.44 | 21379.47 | 89 | 44 | 28466.94 | 26273.53 | 136.64 | 4771 | 36
200 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 205480.76 | 186160.1 | 9792.91 | 95 | 48 | 41029.6 | 37860.09 | 98.47 | 2164 | 36
300 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 200983.16 | 190657.7 | 5695.93 | 97 | 49 | 45527.2 | 41957.08 | 72.84 | 1089 | 36
400 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 198930.75 | 192710.11 | 3852.43 | 98 | 49 | 47579.61 | 43800.58 | 57.03 | 682 | 36
500 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 197385.24 | 194255.62 | 2476.08 | 99 | 50 | 49125.12 | 45176.92 | 47.06 | 503 | 36
600 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 196308.21 | 195332.65 | 1531.49 | 99 | 50 | 50202.15 | 46121.52 | 40.04 | 276 | 21
700 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 195613.76 | 196027.1 | 939.48 | 100 | 50 | 50896.6 | 46713.52 | 34.76 | 96 | 20
800 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 195343.07 | 196297.79 | 738.02 | 100 | 50 | 51167.29 | 46914.98 | 30.54 | 68 | 19
900 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 195103.49 | 196537.37 | 565.22 | 100 | 50 | 51406.87 | 47087.78 | 27.25 | 63 | 18
1000 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194863.91 | 196776.95 | 392.42 | 100 | 50 | 51646.46 | 47260.58 | 24.61 | 58 | 17
1100 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194681.06 | 196959.8 | 271.91 | 100 | 50 | 51829.3 | 47381.1 | 22.43 | 32 | 16
1200 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194535.23 | 197105.63 | 185.51 | 100 | 50 | 51975.14 | 47467.5 | 20.6 | 30 | 15
1300 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194389.39 | 197251.47 | 99.11 | 100 | 50 | 52120.97 | 47553.9 | 19.05 | 28 | 14
1400 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194243.56 | 197397.3 | 12.71 | 100 | 50 | 52266.8 | 47640.3 | 17.72 | 9 | 4
1500 | 259.2 | 185.1429 | High | 192783.5 | 391640.86 | 194177.69 | 197463.17 | 0 | 100 | 50 | 52332.67 | 47653 | 16.55 | 0 | 0
100 | 259.2 | 185.1429 | Low | 98582.5 | 391640.86 | 293183.42 | 98457.44 | 1815.02 | 98 | 25 | 21641.25 | 19951.29 | 103.88 | 812 | 20
200 | 259.2 | 185.1429 | Low | 98582.5 | 391640.86 | 291508.55 | 100132.31 | 319.46 | 100 | 26 | 23316.12 | 21446.85 | 55.85 | 103 | 18
300 | 259.2 | 185.1429 | Low | 98582.5 | 391640.86 | 291256.87 | 100383.99 | 135.51 | 100 | 26 | 23567.8 | 21630.79 | 37.55 | 31 | 15
400 | 259.2 | 185.1429 | Low | 98582.5 | 391640.86 | 291111.04 | 100529.82 | 49.11 | 100 | 26 | 23713.63 | 21717.19 | 28.28 | 27 | 13
500 | 259.2 | 185.1429 | Low | 98582.5 | 391640.86 | 291005.66 | 100635.2 | 0 | 100 | 26 | 23819 | 21766.31 | 22.67 | 0 | 0
100 | 194 | 138.5714 | Low | 98582.5 | 293730.77 | 196584.68 | 97146.09 | 3236.24 | 97 | 33 | 23115.26 | 21315.44 | 110.95 | 1428 | 23
200 | 194 | 138.5714 | Low | 98582.5 | 293730.77 | 193661.91 | 100068.87 | 590.61 | 99 | 34 | 26038.04 | 23961.06 | 62.4 | 180 | 18
300 | 194 | 138.5714 | Low | 98582.5 | 293730.77 | 193187.08 | 100543.69 | 201.01 | 100 | 34 | 26512.86 | 24350.66 | 42.28 | 60 | 16
400 | 194 | 138.5714 | Low | 98582.5 | 293730.77 | 192998.63 | 100732.14 | 75.33 | 100 | 34 | 26701.31 | 24476.34 | 31.87 | 28 | 14
500 | 194 | 138.5714 | Low | 98582.5 | 293730.77 | 192864.81 | 100865.96 | 0 | 100 | 34 | 26835.14 | 24551.67 | 25.57 | 0 | 0
100 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 169353.57 | 124377.2 | 13283.47 | 90 | 42 | 27494.5 | 25377.34 | 131.97 | 4182 | 36
200 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 159463.67 | 134267.1 | 4174.32 | 97 | 46 | 37384.41 | 34486.49 | 89.72 | 1162 | 36
300 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 157148.96 | 136581.82 | 2089.08 | 98 | 46 | 39699.12 | 36571.73 | 63.49 | 516 | 36
400 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 155895.36 | 137835.41 | 981.76 | 99 | 47 | 40952.72 | 37679.04 | 49.06 | 211 | 20
500 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 155274.66 | 138456.11 | 457.73 | 100 | 47 | 41573.42 | 38203.08 | 39.79 | 96 | 18
600 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 155016.04 | 138714.74 | 267.38 | 100 | 47 | 41832.04 | 38393.43 | 33.33 | 34 | 17
700 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 154870.21 | 138860.57 | 180.98 | 100 | 47 | 41977.87 | 38479.83 | 28.63 | 31 | 15
800 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 154724.37 | 139006.4 | 94.58 | 100 | 47 | 42123.71 | 38566.23 | 25.11 | 28 | 14
900 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 154578.54 | 139152.24 | 8.18 | 100 | 47 | 42269.54 | 38652.63 | 22.37 | 6 | 3
1000 | 194 | 138.5714 | Med | 135543.5 | 293730.77 | 154517.58 | 139213.19 | 0 | 100 | 47 | 42330.5 | 38660.81 | 20.14 | 0 | 0
100 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 130481.23 | 163249.54 | 31765.18 | 84 | 56 | 28949.27 | 26718.05 | 138.96 | 6141 | 36
200 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 116491.04 | 177239.73 | 18833.42 | 90 | 60 | 42939.46 | 39649.81 | 103.05 | 3642 | 36
300 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 110794.76 | 182936.02 | 13613.28 | 93 | 62 | 48635.75 | 44869.95 | 77.82 | 2363 | 36
400 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 107455.36 | 186275.41 | 10583.7 | 95 | 63 | 51975.14 | 47899.53 | 62.37 | 1715 | 36
500 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 105081.1 | 188649.67 | 8443.58 | 96 | 64 | 54349.4 | 50039.65 | 52.12 | 1389 | 36
600 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 103193.57 | 190537.2 | 6752.03 | 96 | 65 | 56236.94 | 51731.2 | 44.91 | 1061 | 36
700 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 101690.86 | 192039.91 | 5415.13 | 97 | 65 | 57739.65 | 53068.1 | 39.49 | 870 | 36
800 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 100297.13 | 193433.64 | 4178.67 | 98 | 66 | 59133.37 | 54304.56 | 35.35 | 700 | 36
900 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 99159.8 | 194570.97 | 3178.51 | 98 | 66 | 60270.71 | 55304.72 | 32.01 | 517 | 28
1000 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 98320.77 | 195410.01 | 2453.26 | 99 | 67 | 61109.74 | 56029.98 | 29.18 | 364 | 20
1100 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 97695.54 | 196035.23 | 1925.05 | 99 | 67 | 61734.96 | 56558.18 | 26.78 | 270 | 19
1200 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 97235.69 | 196495.08 | 1549.25 | 99 | 67 | 62194.82 | 56933.98 | 24.71 | 197 | 18
1300 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 96860.69 | 196870.08 | 1251.65 | 99 | 67 | 62569.82 | 57231.58 | 22.93 | 188 | 17
1400 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 96485.69 | 197245.08 | 954.05 | 100 | 67 | 62944.82 | 57529.18 | 21.4 | 154 | 16
1500 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 96110.69 | 197620.08 | 656.45 | 100 | 67 | 63319.82 | 57826.78 | 20.08 | 146 | 16
1600 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95763.25 | 197967.52 | 384.25 | 100 | 67 | 63667.25 | 58098.98 | 18.91 | 96 | 15
1700 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95564.14 | 198166.63 | 248.75 | 100 | 67 | 63866.36 | 58234.48 | 17.84 | 85 | 15
1800 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95423.49 | 198307.29 | 167.12 | 100 | 68 | 64007.02 | 58316.11 | 16.87 | 57 | 14
1900 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95329.74 | 198401.04 | 128.72 | 100 | 68 | 64100.77 | 58354.51 | 16 | 56 | 14
2000 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95235.99 | 198494.79 | 90.32 | 100 | 68 | 64194.52 | 58392.91 | 15.21 | 42 | 14
2100 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95142.24 | 198588.54 | 51.92 | 100 | 68 | 64288.27 | 58431.31 | 14.49 | 28 | 14
2200 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 95048.49 | 198682.29 | 13.52 | 100 | 68 | 64382.02 | 58469.71 | 13.84 | 10 | 5
2300 | 194 | 138.5714 | High | 192783.5 | 293730.77 | 94981.73 | 198749.04 | 0 | 100 | 68 | 64448.78 | 58483.23 | 13.24 | 0 | 0