## Full comparison
capacity_kwh | Solar_kw_DC | EV_load_scenario | total_load_kwh | total_pv_kwh | pv_curtailed_kwh | pv_used_kwh | energy_not_served_kwh | self_sufficiency_percent | pv_utilization_percent | throughput_charge_kwh | throughput_discharge_kwh | estimated_full_cycles | loss_of_load_hours | max_contiguous_lol_hours
100 | 259.2 | Med | 135543.5 | 392886.42 | 264576.47 | 128309.95 | 9229.33 | 93 | 33 | 25946.2 | 23950.41 | 124.54 | 3261 | 36
200 | 259.2 | Med | 135543.5 | 392886.42 | 257055.69 | 135830.73 | 2324.31 | 98 | 35 | 33466.98 | 30855.44 | 80.32 | 653 | 22
300 | 259.2 | Med | 135543.5 | 392886.42 | 255348.54 | 137537.88 | 799 | 99 | 35 | 35174.13 | 32380.75 | 56.22 | 215 | 18
400 | 259.2 | Med | 135543.5 | 392886.42 | 254807.99 | 138078.43 | 348.83 | 100 | 35 | 35714.68 | 32830.92 | 42.75 | 77 | 17
500 | 259.2 | Med | 135543.5 | 392886.42 | 254594.37 | 138292.05 | 199.96 | 100 | 35 | 35928.29 | 32979.79 | 34.35 | 32 | 16
600 | 259.2 | Med | 135543.5 | 392886.42 | 254448.54 | 138437.88 | 113.56 | 100 | 35 | 36074.13 | 33066.19 | 28.7 | 29 | 14
700 | 259.2 | Med | 135543.5 | 392886.42 | 254302.71 | 138583.71 | 27.16 | 100 | 35 | 36219.96 | 33152.59 | 24.67 | 19 | 9
800 | 259.2 | Med | 135543.5 | 392886.42 | 254221.15 | 138665.27 | 0 | 100 | 35 | 36301.52 | 33179.75 | 21.6 | 0 | 0
100 | 259.2 | High | 192783.5 | 392886.42 | 219553.29 | 173333.13 | 21647.53 | 89 | 44 | 28514.78 | 26317.62 | 136.87 | 4815 | 36
200 | 259.2 | High | 192783.5 | 392886.42 | 206923.61 | 185962.81 | 9998.23 | 95 | 47 | 41144.46 | 37966.93 | 98.75 | 2198 | 36
300 | 259.2 | High | 192783.5 | 392886.42 | 202351.82 | 190534.6 | 5832.86 | 97 | 48 | 45716.25 | 42132.29 | 73.15 | 1116 | 36
400 | 259.2 | High | 192783.5 | 392886.42 | 200267.44 | 192618.98 | 3959.9 | 98 | 49 | 47800.63 | 44005.25 | 57.3 | 692 | 36
500 | 259.2 | High | 192783.5 | 392886.42 | 198702.8 | 194183.62 | 2565.93 | 99 | 49 | 49365.27 | 45399.22 | 47.29 | 508 | 36
600 | 259.2 | High | 192783.5 | 392886.42 | 197597.57 | 195288.85 | 1595.35 | 99 | 50 | 50470.5 | 46369.81 | 40.25 | 292 | 22
700 | 259.2 | High | 192783.5 | 392886.42 | 196872.43 | 196013.99 | 975.06 | 99 | 50 | 51195.64 | 46990.1 | 34.96 | 105 | 20
800 | 259.2 | High | 192783.5 | 392886.42 | 196587.41 | 196299.01 | 760.38 | 100 | 50 | 51480.67 | 47204.77 | 30.73 | 69 | 19
900 | 259.2 | High | 192783.5 | 392886.42 | 196347.82 | 196538.6 | 587.58 | 100 | 50 | 51720.25 | 47377.57 | 27.42 | 63 | 18
1000 | 259.2 | High | 192783.5 | 392886.42 | 196108.24 | 196778.18 | 414.78 | 100 | 50 | 51959.83 | 47550.37 | 24.77 | 59 | 17
1100 | 259.2 | High | 192783.5 | 392886.42 | 195909.92 | 196976.5 | 280.01 | 100 | 50 | 52158.15 | 47685.14 | 22.58 | 32 | 16
1200 | 259.2 | High | 192783.5 | 392886.42 | 195764.08 | 197122.34 | 193.61 | 100 | 50 | 52303.99 | 47771.54 | 20.73 | 30 | 15
1300 | 259.2 | High | 192783.5 | 392886.42 | 195618.25 | 197268.17 | 107.21 | 100 | 50 | 52449.82 | 47857.94 | 19.17 | 28 | 14
1400 | 259.2 | High | 192783.5 | 392886.42 | 195472.42 | 197414 | 20.81 | 100 | 50 | 52595.65 | 47944.34 | 17.84 | 14 | 7
1500 | 259.2 | High | 192783.5 | 392886.42 | 195397.76 | 197488.66 | 0 | 100 | 50 | 52670.32 | 47965.15 | 16.65 | 0 | 0
100 | 259.2 | Low | 98582.5 | 392886.42 | 294489.53 | 98396.89 | 1883.54 | 98 | 25 | 21750.87 | 20052.94 | 104.4 | 844 | 20
200 | 259.2 | Low | 98582.5 | 392886.42 | 292754.5 | 100131.91 | 332.54 | 100 | 25 | 23485.9 | 21603.94 | 56.26 | 108 | 18
300 | 259.2 | Low | 98582.5 | 392886.42 | 292489.1 | 100397.32 | 135.95 | 100 | 26 | 23751.3 | 21800.53 | 37.85 | 31 | 15
400 | 259.2 | Low | 98582.5 | 392886.42 | 292343.27 | 100543.15 | 49.55 | 100 | 26 | 23897.13 | 21886.93 | 28.5 | 27 | 13
500 | 259.2 | Low | 98582.5 | 392886.42 | 292237.42 | 100649 | 0 | 100 | 26 | 24002.98 | 21936.48 | 22.85 | 0 | 0
100 | 194.4 | Low | 98582.5 | 294664.96 | 197596.82 | 97068.14 | 3321.05 | 97 | 33 | 23208.72 | 21402.04 | 111.4 | 1469 | 23
200 | 194.4 | Low | 98582.5 | 294664.96 | 194605.62 | 100059.34 | 612.35 | 99 | 34 | 26199.93 | 24110.73 | 62.79 | 188 | 18
300 | 194.4 | Low | 98582.5 | 294664.96 | 194115.9 | 100549.06 | 209.03 | 100 | 34 | 26689.65 | 24514.05 | 42.56 | 65 | 16
400 | 194.4 | Low | 98582.5 | 294664.96 | 193919.97 | 100744.99 | 76.46 | 100 | 34 | 26885.57 | 24646.62 | 32.09 | 28 | 14
500 | 194.4 | Low | 98582.5 | 294664.96 | 193784.92 | 100880.04 | 0 | 100 | 34 | 27020.62 | 24723.08 | 25.75 | 0 | 0
100 | 194.4 | Med | 135543.5 | 294664.96 | 170465.94 | 124199.03 | 13465.73 | 90 | 42 | 27546.65 | 25425.4 | 132.22 | 4225 | 39
200 | 194.4 | Med | 135543.5 | 294664.96 | 160487.24 | 134177.73 | 4273.88 | 97 | 46 | 37525.35 | 34617.25 | 90.06 | 1194 | 37
300 | 194.4 | Med | 135543.5 | 294664.96 | 158131.73 | 136533.23 | 2151.04 | 98 | 46 | 39880.86 | 36740.08 | 63.78 | 534 | 37
400 | 194.4 | Med | 135543.5 | 294664.96 | 156859.29 | 137805.67 | 1026.36 | 99 | 47 | 41153.3 | 37864.77 | 49.3 | 222 | 21
500 | 194.4 | Med | 135543.5 | 294664.96 | 156218.21 | 138446.76 | 483.54 | 100 | 47 | 41794.38 | 38407.59 | 40.01 | 103 | 18
600 | 194.4 | Med | 135543.5 | 294664.96 | 155936.12 | 138728.84 | 271.57 | 100 | 47 | 42076.47 | 38619.56 | 33.52 | 34 | 17
700 | 194.4 | Med | 135543.5 | 294664.96 | 155790.28 | 138874.68 | 185.17 | 100 | 47 | 42222.31 | 38705.96 | 28.8 | 31 | 15
800 | 194.4 | Med | 135543.5 | 294664.96 | 155644.45 | 139020.51 | 98.77 | 100 | 47 | 42368.14 | 38792.36 | 25.26 | 28 | 14
900 | 194.4 | Med | 135543.5 | 294664.96 | 155498.62 | 139166.34 | 12.37 | 100 | 47 | 42513.97 | 38878.76 | 22.5 | 9 | 4
1000 | 194.4 | Med | 135543.5 | 294664.96 | 155433.11 | 139231.85 | 0 | 100 | 47 | 42579.48 | 38891.13 | 20.26 | 0 | 0
100 | 194.4 | High | 192783.5 | 294664.96 | 131747.32 | 162917.64 | 32095.53 | 83 | 55 | 28929.5 | 26699.83 | 138.86 | 6203 | 40
200 | 194.4 | High | 192783.5 | 294664.96 | 117687.48 | 176977.49 | 19099.58 | 90 | 60 | 42989.34 | 39695.78 | 103.17 | 3690 | 40
300 | 194.4 | High | 192783.5 | 294664.96 | 111958.17 | 182706.79 | 13845.35 | 93 | 62 | 48718.65 | 44950.01 | 77.95 | 2395 | 40
400 | 194.4 | High | 192783.5 | 294664.96 | 108584.58 | 186080.38 | 10784.25 | 94 | 63 | 52092.24 | 48011.1 | 62.51 | 1747 | 40
500 | 194.4 | High | 192783.5 | 294664.96 | 106196.5 | 188468.46 | 8631.39 | 96 | 64 | 54480.32 | 50163.96 | 52.25 | 1412 | 40
600 | 194.4 | High | 192783.5 | 294664.96 | 104278.05 | 190386.91 | 6911.36 | 96 | 65 | 56398.77 | 51884 | 45.04 | 1091 | 40
700 | 194.4 | High | 192783.5 | 294664.96 | 102761.42 | 191903.54 | 5561.63 | 97 | 65 | 57915.39 | 53233.73 | 39.61 | 893 | 39
800 | 194.4 | High | 192783.5 | 294664.96 | 101352.38 | 193312.58 | 4311.05 | 98 | 66 | 59324.44 | 54484.31 | 35.47 | 723 | 38
900 | 194.4 | High | 192783.5 | 294664.96 | 100195.47 | 194469.49 | 3292.85 | 98 | 66 | 60481.35 | 55502.51 | 32.12 | 533 | 30
1000 | 194.4 | High | 192783.5 | 294664.96 | 99317.76 | 195347.2 | 2531.95 | 99 | 66 | 61359.06 | 56263.41 | 29.3 | 370 | 20
1100 | 194.4 | High | 192783.5 | 294664.96 | 98682.9 | 195982.06 | 1994.86 | 99 | 67 | 61993.92 | 56800.5 | 26.89 | 286 | 20
1200 | 194.4 | High | 192783.5 | 294664.96 | 98213.9 | 196451.06 | 1610.63 | 99 | 67 | 62462.92 | 57184.72 | 24.82 | 201 | 18
1300 | 194.4 | High | 192783.5 | 294664.96 | 97838.9 | 196826.06 | 1313.03 | 99 | 67 | 62837.92 | 57482.32 | 23.03 | 190 | 17
1400 | 194.4 | High | 192783.5 | 294664.96 | 97463.9 | 197201.06 | 1015.43 | 99 | 67 | 63212.92 | 57779.92 | 21.5 | 156 | 16
1500 | 194.4 | High | 192783.5 | 294664.96 | 97088.9 | 197576.06 | 717.83 | 100 | 67 | 63587.92 | 58077.52 | 20.17 | 147 | 16
1600 | 194.4 | High | 192783.5 | 294664.96 | 96729.2 | 197935.76 | 434.33 | 100 | 67 | 63947.62 | 58361.03 | 19 | 115 | 15
1700 | 194.4 | High | 192783.5 | 294664.96 | 96498.77 | 198166.19 | 269.97 | 100 | 67 | 64178.05 | 58525.39 | 17.93 | 85 | 15
1800 | 194.4 | High | 192783.5 | 294664.96 | 96350.5 | 198314.46 | 181.33 | 100 | 67 | 64326.32 | 58614.03 | 16.96 | 57 | 14
1900 | 194.4 | High | 192783.5 | 294664.96 | 96256.75 | 198408.21 | 142.93 | 100 | 67 | 64420.07 | 58652.43 | 16.08 | 56 | 14
2000 | 194.4 | High | 192783.5 | 294664.96 | 96163 | 198501.96 | 104.53 | 100 | 67 | 64513.82 | 58690.83 | 15.28 | 49 | 14
2100 | 194.4 | High | 192783.5 | 294664.96 | 96069.25 | 198595.71 | 66.13 | 100 | 67 | 64607.57 | 58729.23 | 14.57 | 28 | 14
2200 | 194.4 | High | 192783.5 | 294664.96 | 95975.5 | 198689.46 | 27.73 | 100 | 67 | 64701.32 | 58767.63 | 13.91 | 20 | 10
2300 | 194.4 | High | 192783.5 | 294664.96 | 95893.34 | 198771.62 | 0 | 100 | 67 | 64783.48 | 58795.36 | 13.31 | 0 | 0